## Slide 1: NC Selection Software (AIO)

## Slide 2: NC Selection Software (AIO)
AIO Software Demo
Silencer Selection Summary
Silencer Selection Exercise
Factors Affecting Performance
Agenda

## Slide 3: AIO Software Demo

## Slide 4: NC Selection Software
AIO (All in one software)
Available for “Free” download at:
https://www.priceindustries.com/software/all-in-one/
ALL-IN-ONE Software

## Slide 5: NC Selection Software
Silencer Selection:
Powerful tool for selecting Noise Control Products:
Three(3) Search Types:
- Selection by Scheduled Performance
- Selection by Design Criteria
- Selection by Price Industries Model
ALL-IN-ONE Software

## Slide 6: NC Selection Software
Selections by scheduled performance
ALL-IN-ONE Software

## Slide 7: NC Selection Software
Selection by design criteria
ALL-IN-ONE Software

## Slide 8: NC Selection Software
ALL-IN-ONE Software

## Slide 9: NC Selection Software
By Model
ALL-IN-ONE Software

## Slide 10: Silencer Selection Summary

## Slide 11: NC Selection Software
Silencer Selection Summary

## Slide 12: NC Selection Software
Typical Silencer Schedule
Silencer Selection Summary

## Slide 13: NC Selection Software
Competitor Cross Reference
Silencer Selection Summary

## Slide 14: NC Selection Software
Silencer Selection Summary

## Slide 15: NC Selection Software
Silencer models & options
Schedule creation
Submittal creation
Construction options
Tested Performance
Cross reference
System effects
Silencer Selection Summary

## Slide 16: NC Selection Software
Elbow leg length (non-equal)
Silencer Selection Summary

## Slide 17: NC Selection Software
Resources
Silencer Selection Summary

## Slide 18: NC Selection Software
Silencer Selection:
Project Properties
Shape (Rectangular, Elbow, & Circular, Air Transfer Silencers)
Dimensions
Performance (Insertion Loss & Pressure Drop)
  System Effects
Construction (Material, Gauge, Inlet/Outlet, etc.)
Search Results
Submittals/Schedules
Resources
Competitor Reference
Silencer Selection Summary

## Slide 19: Silencer Selection Exercise

## Slide 20: NC Selection Software
Select the follow schedule in AIO:
Silencer Selection Ex.
Silencer Information |  |  |  | Duct System Information |  |  |  | Dynamic Insertion Loss (dB) |  |  |  |  |  |  |  |  | 
Tag | Width (in) | Height (in) | Length (in) | Air Flow | Flow (CFM) | Velocity (FPM) | PD (in. w.g.) | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k | Notes | Casing Gauge
SA-1 | 12.00 | 12.00 | 36 | Forward | 1000 | 1000 | 0.25 | 5 | 8 | 15 | 30 | 35 | 30 | 23 | 17 | 1-4 | HTL1 CASING
RA-1 | 12.00 | 12.00 | 60 | Reverse | 1000 | 735 | 0.13 | 8 | 12 | 20 | 32 | 33 | 30 | 24 | 16 | 1-4 | HTL1 CASING
SA-2 | 20.00 | 20.00 | 36 | Forward | 1000 | 360 | 0.03 | 5 | 9 | 16 | 26 | 25 | 21 | 16 | 12 | 1-4 | HTL1 CASING
RA-2 | 24.00 | 24.00 | 120 | Reverse | 1000 | 360 | 0.10 | 23 | 24 | 48 | 55 | 55 | 55 | 55 | 46 | 1-4 | HTL1 CASING
Notes: | 
1. | RECTANGULAR STRAIGHT DISSIPATIVE SILENCER
2. | HTL EQUIVALENT TO 10Ga GALVANIZED STEEL CASING
3. | 22GA PERFORATED LINER
4. | FIBERGLASS ACOUSTIC MEDIA
Notes: Printed copies for Reps to come up and do selections

## Slide 21: Factors Affecting Performance

## Slide 22: NC Selection Software
Internal Silencer Geometry
Rectangular
Low velocity
Rectangular
Medium velocity
Rectangular
High velocity
*Based on a 12”Wx12”Hx36”L @ 1000FPM 1 Module D Gap
Factors Affecting Performance
 | Insertion Loss (dB) |  |  |  |  |  |  | 
 | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz
RL | 7 | 10 | 17 | 32 | 37 | 32 | 25 | 19
RM | 5 | 8 | 14 | 27 | 33 | 31 | 23 | 19
RH | 5 | 7 | 13 | 24 | 29 | 27 | 20 | 16
Notes: Printed copies for Reps to come up and do selections

## Slide 23: NC Selection Software
Internal Silencer Geometry
Factors Affecting Performance -Internal Geometry
CS – Circular Medium velocity
CS – Circular High velocity
Best suited for applications with velocities ~ 4,000 fpm These silencers feature a center pod that increases acoustical performance.
These silencers do not have a center pod. This design minimizes pressure drop at high velocities while still providing high levels of insertion loss, up to 8000 fpm.
Notes: Internal geometry of the silencer. On this slide are the three main configurations available for our rectangular model. The first model, the RL, is our low velocity, or high velocity model, which has a nose in and nose out design. The RL is recommended for a velocity range up to 750 FPM. The second model is the RM, our medium velocity model, which as a nose in design with a slightly tapered tail. This design is recommended up to a velocity of 1750 FPM. And the third model, the RH high velocity or low pressure drop design has a nose in and a full tail along the length of the silencer. This model is recommended up to a velocity of 2500 FPM.

## Slide 24: NC Selection Software
Internal Silencer Geometry
Circular Medium velocity
Circular High velocity
*Based on a 14” Diameter 60”L @ 1000FPM
Factors Affecting Performance-Internal Geometry
0.01
0.05
 | Insertion Loss (dB) |  |  |  |  |  |  | 
 | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz
CS Med | 6 | 10 | 26 | 42 | 46 | 46 | 42 | 30
CS High | 5 | 8 | 22 | 39 | 40 | 25 | 17 | 18
Notes: Internal geometry of the silencer. On this slide are the three main configurations available for our rectangular model. The first model, the RL, is our low velocity, or high velocity model, which has a nose in and nose out design. The RL is recommended for a velocity range up to 750 FPM. The second model is the RM, our medium velocity model, which as a nose in design with a slightly tapered tail. This design is recommended up to a velocity of 1750 FPM. And the third model, the RH high velocity or low pressure drop design has a nose in and a full tail along the length of the silencer. This model is recommended up to a velocity of 2500 FPM.

## Slide 25: NC Selection Software
Internal Silencer Geometry – (ERM)
Factors Affecting Performance -Internal Geometry
-Price Industries has a modified tail design resulting in better pressure drop performance.
-Features variable turning ratios depending on internal free Area
Notes: Internal geometry of the silencer. On this slide are the three main configurations available for our rectangular model. The first model, the RL, is our low velocity, or high velocity model, which has a nose in and nose out design. The RL is recommended for a velocity range up to 750 FPM. The second model is the RM, our medium velocity model, which as a nose in design with a slightly tapered tail. This design is recommended up to a velocity of 1750 FPM. And the third model, the RH high velocity or low pressure drop design has a nose in and a full tail along the length of the silencer. This model is recommended up to a velocity of 2500 FPM.

## Slide 26: NC Selection Software
Silencer Media Type:
Factors Affecting Performance – Silencer Type
Absorptive/Dissipative
Film Lined
Packless/ Reactive
 | Insertion Loss (dB) |  |  |  |  |  |  |  | 
 | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz | PD (in w.g.)
Absorptive | 5 | 6 | 11 | 21 | 26 | 24 | 18 | 15 | 0.05
Film Lined | 5 | 6 | 9 | 16 | 23 | 24 | 18 | 13 | 0.05
Pack-less | 3 | 3 | 5 | 12 | 13 | 8 | 7 | 6 | 0.1
*Based on a 12”Wx12”Hx36”L @ 1000FPM 1 Module C Gap
Notes: The next letter A, acoustic media represents how different media types and liner options affect the performance of the silencer. The standard media type for absorptive silencers is glass fiber acoustic media. On the graph of insertion loss versus octave band, this is represented by the blue line. I should also mention, one of the silencer manufacturers does a really good job at promoting the natural fiber so it is an option that is available as well, even though we prefer to use glass fiber, hence the large disclaimers that appear on quotes and submittals. However, it is believed to perform the same as the standard glass fiber.
As you may have noticed, the pressure drop comparison is not represented on this graph as the acoustic media type does not affect the performance of a silencer.
Now, lets look at the green, pink and yellow lines on the graph. The green line represents fiberglass cloth, which is used to protect the acoustic media from erosion at high velocities. We say that fiberglass cloth is acoustically transparent, so this means that it does not affect the performance of the silencer, as you can see the green line and the blue line have the same insertion loss performance.
Tedlar film liner, which provides further protection to the acoustic media however is not acoustically transparent. Adding this option does degrade the performance of the silencer, buy up to 40% in some octave bands. As you can see from the graph, the yellow line, which represents Tedlar liner, has the lowest insertion loss. We add acoustic standoff to the Tedlar so that it does not plug the holes of the perforated liner, as you can see by the pink line, this does bring up the insertion loss.

## Slide 27: NC Selection Software
Silencer Standard Lengths
  Minimum Length = 24” (2’)
  Maximum Length = 120” (10’)
Factors Affecting Performance – Silencer Length
3ft
5ft
7ft
PD = 0.08 in w.g.
*Based on a 24”Wx24”H @ 1000FPM 1 Module D Gap
PD = 0.07 in w.g.
PD = 0.06 in w.g.

## Slide 28: NC Selection Software
Silencer Component “Standard” Size Limits
Factors Affecting Performance – Silencer Module
Component Size Limits:
Width: Maximum 48”
Height: Maximum 48”
Notes: The first letter F for Free Area is denoted by a P.A. Code, or pressure attenuation code. For most silencer models the available pressure codes range from A through to G, where A represents highest free area, or largest air gap through the silencer, and G represents the lowest free area and therefore the tightest air gap.

## Slide 29: NC Selection Software
Silencer Bank Size Limits
Factors Affecting Performance – Silencer Module
Bank Size Limits:
Width: Maximum 450”
Height: Maximum 450”
Larger sizes can be selected by using multiple banks, For example:
Qty-1, 500”W @ 1500 fpm =
QTY-2, 250”W @ 750fpm
Notes: The first letter F for Free Area is denoted by a P.A. Code, or pressure attenuation code. For most silencer models the available pressure codes range from A through to G, where A represents highest free area, or largest air gap through the silencer, and G represents the lowest free area and therefore the tightest air gap.

## Slide 30: NC Selection Software
Number of Modules Example – 36” Wide x 48” High
Factors Affecting Performance – Silencer Module
1 Module
Module Width =36”
W=35”-38”
3 Module
Module Width =12”
1=12”-14”
2 Module
Module Width =18”
3=17”-19”
Notes: The first letter F for Free Area is denoted by a P.A. Code, or pressure attenuation code. For most silencer models the available pressure codes range from A through to G, where A represents highest free area, or largest air gap through the silencer, and G represents the lowest free area and therefore the tightest air gap.

## Slide 31: NC Selection Software
Number of Modules – 36” Wide x 48” High
Factors Affecting Performance – Silencer Module
1 Module
Module Width =36”
W=35”-38”
3 Module
Module Width =12”
1=12”-14”
2 Module
Module Width =18”
3=17”-19”
 | Insertion Loss (dB) |  |  |  |  |  |  |  | 
 | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz | PD (in w.g.)
1 Module | 7 | 10 | 14 | 19 | 15 | 11 | 10 | 8 | 0.11
2 Module | 5 | 9 | 14 | 24 | 26 | 21 | 18 | 14 | 0.14
3 Module | 5 | 8 | 14 | 27 | 33 | 31 | 23 | 19 | 0.16
*Based on a model RM 36”Wx48”Hx36”L @ 1000FPM D Gap
Notes: The first letter F for Free Area is denoted by a P.A. Code, or pressure attenuation code. For most silencer models the available pressure codes range from A through to G, where A represents highest free area, or largest air gap through the silencer, and G represents the lowest free area and therefore the tightest air gap.

## Slide 32: NC Selection Software
PA codes range from 60-20% corresponding from A to G
Factors Affecting Performance – Silencer Gap Code
Notes: The first letter F for Free Area is denoted by a P.A. Code, or pressure attenuation code. For most silencer models the available pressure codes range from A through to G, where A represents highest free area, or largest air gap through the silencer, and G represents the lowest free area and therefore the tightest air gap.

## Slide 33: NC Selection Software
System Effect
  Accounts for added pressure drop due to less than ideal inlet and outlet conditions
  System Effect factors are available from:
    AMCA Fans & Systems
    SMACNA HVAC Systems Duct Design
    ASHRAE Applications Handbook
    Price Engineering Guide
Factors Affecting Performance
Notes: System Effect is defined as the negative impact on performance that results when a unit is connected to a duct system. What this means is that the installed performance can deviate from the tested lab performance. Lab conditions are considered ideal to provide a fair comparison between products, however the actual installed conditions are usually somewhat less than ideal due to various constraints often beyond the control of the designer. (space, cost, legacy systems etc)
Therefore when the installed conditions deviate significantly from the tested lab conditions one needs to consider how the silencer will perform when installed versus the catalog performance. The catalog performance is based on the current silencer ASTM E477 testing standard which requires at least 5 equivalent duct diameters upstream, and at least 10 equivalent duct diameters downstream. These conditions seldom exist in the real world.
How do we account for system effect? There are several sources that you can draw upon. AMCA, SMACNA, ASHRAE Applications handbook, and the pages 15-17 of the Price Engineering guide (which you have in front of you)
System Effect is Velocity dependant and accounts for added pressure drop due to less than ideal duct conditions.
System Effect is important when installed conditions of a silencer deviate significantly from the laboratory testing conditions
System Effect Factors are available from:
    AMCA Fans and Systems
    SMACNA HVAC Systems Duct Design
    ASHRAE Applications Handbook
    Price Engineering Guide

## Slide 34: NC Selection Software
System Effect
  Pdsystem effect = Pdcatalog x Factorinlet x Factoroutlet
Factors Affecting Performance
Notes: Here is a table of the Silencer system effect factors as shown in the Price Silencer Engineering Guide. As you can see we need to take into consideration the inlet and outlet conditions for the silencer in order to adequately account for system effect. So lets start with a simple example to illustrate the concept with some actual numbers.

## Slide 35: NC Selection Software
System Effect
Factors Affecting Performance
50% Free Area
~ 3000 FPM
Duct Design at 1500 FPM
Silencer PD = 0.25 “ w.g.
PD System Effect = 0.50 “ w.g.
Silencer PD = 0.25 “ w.g.

## Slide 36: NC Selection Software
System Effect
  Specify silencers designed to be close coupled
    AHRI Certified quiet terminal units
Factors Affecting Performance
Single Duct Supply
Fan Powered Terminal
Venturi Valves

## Slide 37: Questions?