## Slide 1: Noise Control Products & Solutions

## Slide 2: Copyright Materials
This presentation is protected by U.S. and international copyright laws. Reproduction, distribution, display and use of this presentation without written permission of the speaker is prohibited. ® Price Industries, Incorporated 2020
Noise Control

## Slide 3: Noise Control
Mauricio Salinas P.Eng.
Application Engineering Manager, Noise Control
  Oversees the noise application engineering team focusing in noise control solutions, and product development
  10+ Years of Experience in HVAC Industry
  Primarily focused on commercial building HVAC acoustics
Presenter

## Slide 4: Noise Control
Sound Laboratory – 5 minutes
Product Overview – 15 minutes
Acoustic Analysis – 10 minutes
Noise Control Solutions – 10 minutes
Agenda

## Slide 5: Noise Control Laboratory

## Slide 6: Noise Control
Noise Control Laboratory
Notes: The Noise Control Laboratory is a state-of-the-art acoustical test facility.
From ground breaking through commissioning, great care was taken to ensure that the noise data produced by the lab would be accurate, repeatable, and the most reliable in the industry.
At peak capacity, the lab is capable of testing over 30 silencers a week. This high testing output has enabled Price to develop the most thoroughly tested product line in the industry.
All components of the lab have been designed to meet or exceed both current and future versions of ASTM E477 Standard for testing acoustical duct silencers.
The solid concrete Sound Source Chambers can generate over 100 decibels (dB) of sound pressure which allows us to attain accurate insertion loss measurements for long silencers.
This gives us the flexibility to test a wide range of products including fan systems, air handling units, and silencers.
The Control Center houses the heart of the operation; a data acquisition system, frequency analyzer, and sound generator that leave nothing to chance.
The Test Duct Work employed in the system had to be designed to minimize sound break-out and break-in of the high test signals produced by the Source Chambers. Multiple layers of sheet metal, drywall mass, and insulation were employed to keep the sound power levels in the general lab area below 70 dB.
The Fan Room consists of a vane axial fan that can produce over 25,000 CFM at 4 in. of static pressure. To ensure that quiet acoustically treated air is used for silencer testing, a range of different noise control solutions are employed including axial fan silencers (AFS), rectangular silencers (RL), acoustical plenums, and custom elbow plenums. Two airflow measuring stations are used to obtain accurate airflow and pressure drop data.
As a part of Price’s ongoing commitment to quality and innovation, the laboratory is accredited by NIST’s National Voluntary Laboratory Accreditation Program (NVLAP) for testing in accordance with ASTM E477. The NVLAP accreditation audits the lab management systems and technical capabilities and ensures that systems are in place to guarantee the best data possible.

## Slide 7: Noise Control
Noise Control Laboratory

## Slide 8: Noise Control
Test Method – ASTM-E477-20
Sound Source
Ductwork
Reverberant Room
Notes: Witness tests
Lab visits
Tech center visits
Lab accreditations

## Slide 9: Noise Control
NVLAP Accreditation
  Certifies laboratory is technically qualified and competent to carry out specific tests
Noise Control Laboratory

## Slide 10: Product Overview

## Slide 11: Noise Control
Product Categories
Absorptive | Film Lined | Packless | Air Transfer
Notes: The second most common silencer is the elbow type silencer. These are typically used where there is not enough space for a standard rectangular silencer, such as in short runs of duct. However the elbow silencer generally has higher pressure drop than the rectangular silencer, but has an increase in the high band performance.

## Slide 12: Noise Control
Rectangular Silencers
  Most common type of silencer
  Lowest cost
  Breakout noise reduced using heavier gauge casing
Product Categories
Notes: Typical insulation good for up to 250F … optional insulation up to 1000F

## Slide 13: Noise Control
Internal Silencer Geometry
Product Categories
RL - Rectangular
Low velocity
RM - Rectangular
Medium velocity
RH - Rectangular
High velocity
Ideal for applications that require very high insertion loss.
The sloped tail provides an optimal balance between insertion loss & pressure drop.
Minimizes pressure drop for applications with high air velocities or poor outlet conditions.

## Slide 14: Noise Control
Elbow Silencers
Where standard rectangular silencers will not fit
Generated noise should be considered
Recommended velocity below 1500 fpm (can work at higher fpm, special attention to gauge and location)
Product Categories

## Slide 15: Noise Control
Internal Silencer Geometry – (ERM)
Product Categories
-Price Industries has a modified tail design resulting in better pressure drop performance.
-Only manufacturer featuring variable turning ratios depending on internal free Area
Notes: Internal geometry of the silencer. On this slide are the three main configurations available for our rectangular model. The first model, the RL, is our low velocity, or high velocity model, which has a nose in and nose out design. The RL is recommended for a velocity range up to 750 FPM. The second model is the RM, our medium velocity model, which as a nose in design with a slightly tapered tail. This design is recommended up to a velocity of 1750 FPM. And the third model, the RH high velocity or low pressure drop design has a nose in and a full tail along the length of the silencer. This model is recommended up to a velocity of 2500 FPM.

## Slide 16: Noise Control
Circular Silencers
  Round duct applications
  Higher velocity up to 8000 fpm
  Acoustic media surrounding entire silencer provides high transmission loss
Product Categories

## Slide 17: Noise Control
Galvanized (Standard)
    G90 Finish
Satin Coat (Galvanneal)
    Paintable finish
Aluminum
    Light Weight
    Outdoor applications
    Corrosive applications
Stainless Steel (304 & 316)
    Outdoor applications
    Corrosive applications
Product Categories

## Slide 18: Noise Control
Painted Silencers Available
Product Categories

## Slide 19: Noise Control
22 Gauge (CL1)
18 Gauge (CL2)
16 Gauge (HTL1)
10 Gauge (HTL2)
Thicker material prevents
sound “breakout”
Product Categories

## Slide 20: Noise Control
Product Categories

## Slide 21: Noise Control
Absorptive Silencers
  Casing
  Perforated Liner
  Acoustic Media
    Glass Fiber
    Natural Cotton Fiber
    Mineral Wool
Product Categories

## Slide 22: Noise Control
Fiberglass Cloth Liner
  Woven fiberglass cloth
  High air velocities
  Prevents acoustic media erosion
Product Categories

## Slide 23: Noise Control
Film Lined Silencers
  Polymer liner + acoustic standoff
  Applications requiring contaminant free environment
  Hospital grade
Product Categories

## Slide 24: Noise Control
Packless
  No acoustic media
  Applications requiring contaminant free environment
  Cleanable / Hospital grade
  For applications with extremely high air quality standards
Product Categories

## Slide 25: Noise Control
    Air Transfer Silencers - Transfer Air / Block Sound
    Maintain privacy
    Minimize intrusive noise
    Common return air plenum
    Various liner options
Product Categories

## Slide 26: Noise Control
Cross-Talk Silencers
Un-ducted air transfer
Low air volumes
Product Categories

## Slide 27: Noise Control
Product Categories

## Slide 28: Noise Control
Product Categories

## Slide 29: Noise Control
Transfer Silencer
4” thick
Installed behind return air grilles
Can be provided with powdercoat paint finish
Product Categories

## Slide 30: Noise Control
RAS Silencers – Return Air Silencers
4” thick
Installed behind return air grilles
Can be provided with powdercoat paint finish
Product Categories
Ducted
Wall
Ceiling

## Slide 31: Noise Control
Return Silencer close coupled with return grille
Product Categories

## Slide 32: Noise Control
Return Air Canopy
7” height
Easy Installation – Sits on ceiling grid
Low Cost
Product Categories

## Slide 33: Noise Control
Return Air Canopy
Product Categories

## Slide 34: Noise Control
Main point: NR is equal or greater than ceiling tile
Product Categories

## Slide 35: Noise Control
Custom Silencers
  Outlets of fans or AHU
  Unique duct configurations
  Extremely high insertion loss requirements
Product Categories

## Slide 36: Noise Control
Acoustic Louvers
Product Categories

## Slide 37: Noise Control
Product Categories
Blade & Airfoil Louver styles
  6”, 8”, & 12” depths
  Aluminum, stainless & galvanneal
  7 durable finishes

## Slide 38: Noise Control
Acoustic Panels
Product Categories
Notes: An product that we have been developing over the last few years are Acoustic Panels. Why Price Acoustic Panels? .. They are an excellent option to maintain radiated noise at adequate levels. They are typically located close to the noise source. Noise sources can be Air Handling units, Chillers, and Mechanical Equipment . Also, because the sound energy created by a source can be transmitted along multiple paths to the receiver, the incorporation of acoustic panel walls in a mechanical room for example can provide a considerable reduction in noise transmission. Thus, it becomes a potential and effective solution for controlling noise.

## Slide 39: Noise Control
Acoustic Panels
Solid metal outer casing, fiberglass acoustic media with a perforated or solid inner liner
Provides transmission loss (STC) & sound absorption (NRC) for various applications
Product Categories

## Slide 40: Noise Control
Models:
  2” thickness
  4” thickness
  6” thickness
  Custom available
Construction:
  Tongue & groove, H-Channel
  22Ga, 18Ga, & 16Ga
  Galvanized steel, Aluminum, 304SS, 316SS, & Galvanneal painted
  Fiberglass acoustic media with various liners
Acoustic Panels

## Slide 41: Noise Control
Additional features:
  Rigid fiber media
  Mineral wool media
  Polymer film liner
  Fiber glass cloth
  Painted finish
  Heavy gauges 14Ga, 12Ga, 10Ga
  Access doors with wire glass view ports
  Removable panels
  Customized windows
  Integration with silencers & louvers
Product Overview
Notes: Additional features:
  Rigid fiber media
  Mineral wool media
  Polymer film liner
  Fiber glass cloth
  Painted finish
  Custom heavy gauges 16Ga, 14Ga, 12Ga, 10Ga
  Access doors with wire glass view ports
  Removable panels
  Customized windows
  Integration with silencers & louvers

## Slide 42: Noise Control
  Enclosures shipped knocked down for field assembly
  Complete with:
    Trim
    Mounting channels
    Caulking
    Hardware
    Assembly drawings
Product Categories

## Slide 43: Noise Control
AMP (Architectural Modular Panel):
- Tested Under ASTM-C423-17
NRC- 0.95 (2” Thick)
Powder Coated
Improves speech intelligibility
Ideal for Boardrooms/ Offices
Acoustic Panels

## Slide 44: Acoustic Analysis

## Slide 45: Noise Control
Acoustic Environments
Acoustic Analysis
Notes: In our commercial HVAC industry there are a variety of acoustic environments we are involved with.
From operating rooms to …. Each one of these environments have their own characteristics, challenges and design goals.
For example in schools and theaters we need to minimize fan noise so that a teacher can communicate effectively and concert goers can enjoy music.
In hospital rooms and office spaces privacy is needed so confidential conversations are not over heard.
For each environment different types of noise control can be applied to suit the application
Sound is an important part of the environment that we live in. It affects our ability to communicate, work productively, sleep.
Concert hall you can the hear the music, enjoy the performance, conference room needs to talk without hearing or being heard by occupants of adjacent rooms. Hospital requires privacy between rooms, and environment quite enough to sleep well in. Classrooms you don’t want ot noise to affect he ability of the students to hear and learn.
The acoustic needs and requirements depend on the space’s intended use.
Various acoustical environments that we typically analyze to determine if noise control is required.
  Hospitals and offices – patient room noise transfer, privacy
  Schools and theaters - fan noise
  Different types of noise control can be applied to suit the application, such as hospitals may require increased air quality and film lined or packless type silencers

## Slide 46: Noise Control
Acoustic Environments
  The Acoustical Environment: "Dead"  "Live"
  Use of the room dictates the acoustical goals
    Highly reflective = "live"
    Very absorptive = "dead"
  Requirements of most rooms will fall somewhere between these two extremes
Acoustic Analysis

## Slide 47: Noise Control
  Air Handling Unit
  Chiller
  Terminal Unit
Acoustic Analysis
  Ductwork
  Walls, Ceilings/Floors
  Open/Exposed
  Conference Room
  Classroom
  Property Line
Sound Power, dB
Attenuation, dB
Sound Pressure, dB
  SOURCE
  PATH
  RECEIVER
3 Aspects to consider

## Slide 48: Noise Control
  Duct lining & Elbows
  Silencers & Panels
  Relocated Source?
Acoustic Analysis
  Duct lining & Elbows
  Silencers & Panels
  Relocated Source?
  MER Adjacencies
  Exposed Terminals
  Transfer air flanking
Typically longer path
Often shorter path
Uh Oh!
  SUPPLY
  RETURN
  RADIATED
3 Types to consider

## Slide 49: Noise Control
Common Sound Paths
  Path A – Structure born path
  Path B – Airborne path
  Path C – Duct born path
Acoustic Analysis

## Slide 50: Noise Control
Example AHU Return Path Analysis
  Determine expected sound level in space
Acoustic Analysis

## Slide 51: Noise Control
Example
  Determine reduction in sound required
    Space estimated at NC >65
    Target criteria of NC40
    Calculate Required IL
Acoustic Analysis

## Slide 52: Noise Control
Acoustic Analysis Software:
  Powerful HVAC modelling tool for:
    Sale Representatives
    Engineers
    Architects
    Consultants
    Acousticians
    Contractors
    Educators
Acoustic Analysis

## Slide 53: Noise Control
Acoustic Analysis

## Slide 54: Noise Control
Acoustic Analysis

## Slide 55: Noise Control
A few of our users…
Acoustic Analysis

## Slide 56: Noise Control
AIO (All in one software)
Available for “Free” download at:
https://www.priceindustries.com/software/all-in-one/
AIO Software

## Slide 57: Noise Control
AIO Software

## Slide 58: Noise Control
Competitive landscape
Acoustic Analysis
Dynasonics / Pottorff – Acoustics Information Modeling - AIM
    Discontinued support in 2019. No longer active.
Trane – Trane Acoustics Program - TAP
    Outdated. $495 cost per license + annual licensing fee
Vibro-Acoustics – VA Design
    Web/Cloud based platform

## Slide 59: Solutions

## Slide 60: Noise Control
Solutions
chiller enclosure
Reston Library
reston, va

## Slide 61: Noise Control
Solutions
Rooftop Chiller - NY, NY (2012)
Rooftop chiller silencers
Mixed use luxury building
New york City, ny

## Slide 62: Noise Control
Solutions
Acoustic plenums
Mercy hospital joplin
Joplin, mo

## Slide 63: Noise Control
Solutions
Acoustic barrier wall
CSM bakery
Atlanta, ga

## Slide 64: Noise Control
Solutions
WALL MOUNT ACOUSTIC PANELS
CSM bakery
Atlanta, ga

## Slide 65: Noise Control
Solutions
Acoustic barrier wall
CSM bakery
Atlanta, ga

## Slide 66: Noise Control
Solutions
Fan Enclosures
Return Air silencers
Poslinelli headquaRters
Kansas city, mo

## Slide 67: Noise Control
Solutions
Louver Penthouse
Hotel Georgia Vancouver, 2011
Notes: Hotel Georgia Vancouver, 2011
Will U, EH Price – Vancouver
Rosewood Hotel Georgia protected heritage property by city of Vancouver. 2011 Renovation project.
Concern of noise and aesthetics from new cooling tower for residential building siting behind hotel.

## Slide 68: Noise Control
Solutions
Enclosure- warming HUT
The Forks
Winnipeg, MB
Notes: Hotel Georgia Vancouver, 2011
Will U, EH Price – Vancouver
Rosewood Hotel Georgia protected heritage property by city of Vancouver. 2011 Renovation project.
Concern of noise and aesthetics from new cooling tower for residential building siting behind hotel.

## Slide 69: Noise Control
Solutions
chiller enclosure
Residential Condo
Winnipeg, MB

## Slide 70: Noise Control
Solutions
cu enclosure
Sarnia, ON

## Slide 71: Noise Control
Solutions
Architectural Ceiling Panels
PRCN , WINNIPEG, mb

## Slide 72: Questions?